## READ ME
This spreadsheet allows one to perform the calculations of system Minimum Outdoor Air Intake Vot under the Ventilation Rate Procedure in ASHRAE Standard 62.1-2004, including the calculations of System Ventilation Efficiency Ev. This approach first appeared in addendum 62n to Standard 62.1-2001. There are two methods for accounting for System Efficiency in the calculation of Vot, the default values in Table 6-3 and the calculation method in Appendix A. Worksheets 6-3 IP and 6-3 SI contain the calculation method based on Table 6-3 in IP and SI units respectively. Worksheets AppA IP and AppA SI contain the complete calculation method based on Appendix A in IP and SI units.

## 6-3 IP
READ THIS FIRST To use this spreadsheet, identify the zones served by the system being designed and list them in row 4. Then select the space type using the pull down menus in row 5. For each zone, enter the values in all yellow shaded cells, plus the total number of occupants expected to be served by the system in cell C20. The values used for Vpz and Vpzm depend on whether one is designing a CAV or VAV system. Notes in bold text are included below that explain these distinctions. NOTE: Various sums and formulas in column C (in boxes) are based on the individual zone data entered from column C through column Z. If the system, has more than 24 zones, then the sums and formulas in column C need to be modified to include all the zones.
ZONE LEVEL
| Zones served by system | Zone 1 | Zone 2 | Zone 3 | Zone 4
| Space type (select from pull-down list) | Office space | Office space | Conference / meeting | Conference / meeting | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space
Az | Floor area of zone, ft2 | 3340 | 4000 | 2500
Pz | Zone population, largest # of people expected to occupy zone | 20 | 32 | 70
Rp | People outdoor air rate from Table 6.1, cfm/person | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Ra | Area outdoor air rate from Table 6.1, cfm/ft2 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
Pz*Rp |  | 100 | 160 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Az*Ra |  | 200.4 | 240 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ez | Zone air distribution effectiveness, Table 6.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Voz | Outdoor airflow to the zone corrected for zone air distribution effectiveness, (Pz*Rp + Az*Ra)/Ez, cfm | 300.4 | 400 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vpz | Primary airflow to zone from air handler. In VAV systems, use the design value. cfm | 2600 | 3400 | 4000
Vpzm | The minimum value of the primary airflow to zone from air handler. In CAV systems, Vpzm = Vpz. cfm | 650 | 850 | 1000
Zp | Primary outdoor air fraction, Voz/Vpzm | 0.46215 | 0.47059 | 0.5 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SYSTEM LEVEL
Ps | System population, maximum simultaneious # of occupants of space served by system | 80
D | Occupant diversity, ratio of system peak occupancy to sum of space peak occupancies, = Ps/SPz | 0.65574
Vou | Uncorrected outdoor air intake, = D*SRp*Pz +SRa*Az, cfm | 990.4
Xs | Mixing ratio at primary air handler of uncorrected outdoor air intake to system primary flow, = Vou/Vps | 0.09904 | Not used in calculation
SYSTEM EFFICIENCY
Max Zp | Max Zp | 0.5
Ev | System ventilation efficiency, Table 6.3 based on maxZp | 0.6
Percent outdoor air intake
Vot | Minimum outdoor air intake, Vou/Ev, cfm | 1650.6667 |  | 16.51% | = Vot/Sum of Vpz
| Space type | Rp (cfm/per) | Ra (cfm/ft2)
| Art classroom | 10 | 0.18
| Auditorium seating area | 5 | 0.06
| Bank vaults/safe deposit | 5 | 0.06
| Barber shop | 7.5 | 0.06
| Barracks sleeping areas | 5 | 0.06
| Bars, cocktail lounges | 7.5 | 0.18
| Beauty and nail salons | 20 | 0.12
| Bedroom/Living Room | 5 | 0.06
| Booking/waiting | 7.5 | 0.06
| Bowling alley (seating) | 10 | 0.12
| Cafeteria / fast food dining | 7.5 | 0.18
| Cell | 5 | 0.12
| Classrooms (age 9 plus) | 10 | 0.12
| Classrooms (ages 5-8) | 10 | 0.12
| Coin operated laundries | 7.5 | 0.06
| Computer (not printing) | 5 | 0.06
| Computer Lab. | 10 | 0.12
| Conference / meeting | 5 | 0.06
| Corridors | 0 | 0.06
| Courtrooms | 5 | 0.06
| Daycare (through age 4) | 10 | 0.18
| Dayroom | 5 | 0.06
| Disco/dance floors | 20 | 0.06
| Gambling casinos | 7.5 | 0.18
| Game arcades | 7.5 | 0.18
| Guard stations | 5 | 0.06
| Gym, stadium (play area) | 0 | 0.3
| Health club/aerobics room | 20 | 0.06
| Health club/weight rooms | 20 | 0.06
| Lecture Classroom | 7.5 | 0.06
| Lecture Hall (fixed seats) | 7.5 | 0.06
| Legislative chambers | 5 | 0.06
| Libraries | 5 | 0.12
| Lobbies | 5 | 0.06
| Lobbies/prefunction | 7.5 | 0.06
| Main entry lobbies | 5 | 0.06
| Mall common areas | 7.5 | 0.06
| Media Center | 10 | 0.12
| Multi-purpose assembly | 5 | 0.06
| Multi-use Assembly | 7.5 | 0.06
| Museums (Children’s) | 7.5 | 0.12
| Museums/Galleries | 7.5 | 0.06
| Music/theater/dance | 10 | 0.06
| Office space | 5 | 0.06
| Pet shops (animal areas) | 7.5 | 0.18
| Pharmacy (prep. area) | 5 | 0.18
| Photo studios | 5 | 0.12
| Places of religious worship | 5 | 0.06
| Reception areas | 5 | 0.06
| Restaurant dining rooms | 7.5 | 0.18
| Sales (except as below) | 7.5 | 0.12
| Science laboratories | 10 | 0.18
| Shipping/Receiving | 0 | 0.12
| Spectator areas | 7.5 | 0.06
| Sports arena (play area) | 0 | 0.3
| Stages, studios | 10 | 0.06
| Storage rooms | 0 | 0.12
| Supermarket | 7.5 | 0.06
| Swimming (pool & deck) | 0 | 0.48
| Telephone/data entry | 5 | 0.06
| Transportation waiting | 7.5 | 0.06
| Warehouses | 0 | 0.06
| Wood/metal shop | 10 | 0.18

## 6-3 SI
READ THIS FIRST To use this spreadsheet, identify the zones served by the system being designed and list them in row 4. Then select the space type using the pull down menus in row 5. For each zone, enter the values in all yellow shaded cells, plus the total number of occupants expected to be served by the system in cell C20. The values used for Vpz and Vpzm depend on whether one is designing a CAV or VAV system. Notes in bold text are included below that explain these distinctions. NOTE: Various sums and formulas in column C (in boxes) are based on the individual zone data entered from column C through column Z. If the system, has more than 24 zones, then the sums and formulas in column C need to be modified to include all the zones.
ZONE LEVEL
| Zones served by system | Zone 1 | Zone 2 | Zone 3 | Zone 4
| Space type (select from pull-down list) | Lobbies/prefunction | Office space | Classrooms (age 9 plus) | Conference / meeting | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space
Az | Floor area of zone, m2 | 100 | 100 | 100 | 50
Pz | Zone population, largest # of people expected to occupy zone | 20 | 4 | 20 | 10
Rp | People outdoor air rate from Table 6.1, L/s-person | 3.8 | 2.5 | 5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Ra | Area outdoor air rate from Table 6.1, L/s-m2 | 0.3 | 0.3 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Pz*Rp |  | 76 | 10 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Az*Ra |  | 30 | 30 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ez | Zone air distribution effectiveness, Table 6.2 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Voz | Outdoor airflow to the zone corrected for zone air distribution effectiveness, (Pz*Rp + Az*Ra)/Ez, L/s | 117.7778 | 44.4444 | 177.7778 | 44.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vpz | Primary airflow to zone from air handler. In VAV systems, use the design value. L/s | 600 | 600 | 600 | 600
Vpzm | The minimum value of the primary airflow to zone from air handler. In CAV systems, Vpzm = Vpz. L/s | 600 | 600 | 600 | 600
Zp | Primary outdoor air fraction, Voz/Vpzm | 0.1963 | 0.074074 | 0.2963 | 0.074074 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
SYSTEM LEVEL
Ps | System population, maximum simultaneious # of occupants of space served by system | 25
D | Occupant diversity, ratio of system peak occupancy to sum of space peak occupancies, = Ps/SPz | 0.46296
Vou | Uncorrected outdoor air intake, = D*SRp*Pz +SRa*Az, L/s | 232.6852
Xs | Mixing ratio at primary air handler of uncorrected outdoor air intake to system primary flow, = Vou/Vps | 0.096952 | Not used in calculation
SYSTEM EFFICIENCY
Max Zp | Max Zp | 0.2963
Ev | System ventilation efficiency, Table 6.3 based on maxZp | 0.8
Percent outdoor air intake
Vot | Minimum outdoor air intake, Vou/Ev, L/s | 290.8565 |  | 12.12% | = Vot/Sum of Vpz
| Space type | Rp (L/s-per) | Ra (L/s-m2)
| Art classroom | 5 | 0.9
| Auditorium seating area | 2.5 | 0.3
| Bank vaults/safe deposit | 2.5 | 0.3
| Barber shop | 7.5 | 0.3
| Barracks sleeping areas | 2.5 | 0.3
| Bars, cocktail lounges | 3.8 | 0.9
| Beauty and nail salons | 10 | 0.6
| Bedroom/Living Room | 2.5 | 0.3
| Booking/waiting | 3.8 | 0.3
| Bowling alley (seating) | 5 | 0.6
| Cafeteria / fast food dining | 3.8 | 0.9
| Cell | 2.5 | 0.6
| Classrooms (age 9 plus) | 5 | 0.6
| Classrooms (ages 5-8) | 5 | 0.6
| Coin operated laundries | 3.8 | 0.3
| Computer (not printing) | 2.5 | 0.3
| Computer Lab. | 5 | 0.6
| Conference / meeting | 2.5 | 0.3
| Corridors | 0 | 0.3
| Courtrooms | 2.5 | 0.3
| Daycare (through age 4) | 5 | 0.9
| Dayroom | 2.5 | 0.3
| Disco/dance floors | 10 | 0.3
| Gambling casinos | 3.8 | 0.9
| Game arcades | 3.8 | 0.9
| Guard stations | 2.5 | 0.3
| Gym, stadium (play area) | 0 | 0.3
| Health club/aerobics room | 10 | 0.3
| Health club/weight rooms | 10 | 0.3
| Lecture Classroom | 3.8 | 0.3
| Lecture Hall (fixed seats) | 3.8 | 0.3
| Legislative chambers | 2.5 | 0.3
| Libraries | 2.5 | 0.6
| Lobbies | 2.5 | 0.3
| Lobbies/prefunction | 3.8 | 0.3
| Main entry lobbies | 2.5 | 0.3
| Mall common areas | 3.8 | 0.3
| Media Center | 5 | 0.6
| Multi-purpose assembly | 2.5 | 0.3
| Multi-use Assembly | 3.8 | 0.3
| Museums (Children’s) | 3.8 | 0.6
| Museums/Galleries | 3.8 | 0.3
| Music/theater/dance | 5 | 0.3
| Office space | 2.5 | 0.3
| Pet shops (animal areas) | 3.8 | 0.9
| Pharmacy (prep. area) | 2.5 | 0.9
| Photo studios | 2.5 | 0.6
| Places of religious worship | 2.5 | 0.3
| Reception areas | 2.5 | 0.3
| Restaurant dining rooms | 3.8 | 0.9
| Sales (except as below) | 3.8 | 0.6
| Science laboratories | 5 | 0.9
| Shipping/Receiving | 0 | 0.6
| Spectator areas | 3.8 | 0.3
| Sports arena (play area) | 0 | 0.3
| Stages, studios | 5 | 0.3
| Storage rooms | 0 | 0.6
| Supermarket | 3.8 | 0.3
| Swimming (pool & deck) | 0 | 2.4
| Telephone/data entry | 2.5 | 0.3
| Transportation waiting | 3.8 | 0.3
| Warehouses | 0 | 0.3
| Wood/metal shop | 5 | 0.9

## AppA IP
READ THIS FIRST To use this spreadsheet, identify the zones served by the system being designed and list them in row 11. Then select the space type using the pull down menus in row 12. For each zone, enter the values in all yellow shaded cells, plus the total number of occupants expected to be served by the system in cell C36. The values used for Vpz, Vdz and Vdzm depend on whether one is designing a CAV or VAV system. Notes in bold text are included below that explain these distinctions. NOTE: Various sums and formulas in column C (in boxes) are based on the individual zone data entered from column C through column Z. If the system, has more than 24 zones, then the sums and formulas in column C need to be modified to include all the zones.
RESULTS
Vot | Minimum outdoor air intake, Vou/Ev, cfm | 1610.6172
| Percent outdoor air intake, Vot/Vps | 64.42%
Ev | System ventilation efficiency | 0.87091
ZONE LEVEL
| Zones served by system | Zone 1 | Zone 2 | Zone 3 | Zone 4
| Space type (select from pull-down list) | Lobbies/prefunction | Office space | Classrooms (age 9 plus) | Conference / meeting | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space
Az | Floor area of zone, ft2 | 3340 | 4000 | 2500
Pz | Zone population, largest # of people expected to occupy zone | 20 | 32 | 70
Rp | People outdoor air rate from Table 6.1, cfm/person | 7.5 | 5 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Ra | Area outdoor air rate from Table 6.1, cfm/ft2 | 0.06 | 0.06 | 0.12 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
Pz*Rp |  | 150 | 160 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Az*Ra |  | 200.4 | 240 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Voz | Outdoor airflow to the zone corrected for zone air distribution effectiveness, (Pz*Rp + Az*Ra)/Ez, cfm | 350.4 | 400 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vpz | Primary airflow to zone from air handler (intake plus recirculated air, but not local recirculation such as at mixing boxes), cfm. In VAV systems, use the design value. | 650 | 850 | 1000
Vdz | Supply/discharge to zone including primary air Vpz and locally recirculated air, cfm. In VAV systems, use the design value. | 2600 | 3400 | 4000
Vdzm | Minimum supply/discharge to zone used to calculate Ev, cfm. In CAV systems, Vdzm = Vdz. In VAV systems, Vdzm is the minimum expected value of Vdz. | 2600 | 3400 | 4000
Zd | Outdoor air fraction required in air discharged to zone, = Voz/Vdzm | 0.13477 | 0.11765 | 0.25 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Ep | Primary air fraction to zone, = Vpz/Vdz (=1 for single duct and single zone systems) | 0.25 | 0.25 | 0.25 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Er | Fraction of secondary recirc to zone representative of system average, only applies if Ep<1. For plenum return =0. For duct return with local secondary recirc =1. | 0.8 | 0.8 | 0.8
Ez | Zone air distribution effectiveness, Table 6.2 | 1 | 1 | 1
Fa | Fraction of supply air to zone from sources outside zone, = Ep + (1-Ep)*Er | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fb | Fraction of supply air to zone from full mixed primary air, = Ep = Vpz/Vdz | 0.25 | 0.25 | 0.25 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Fc | Fraction of outdoor air to zone from sources outside zone, = 1 - (1-Ez) * (1-Er) * (1-Ep) | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SYSTEM LEVEL
Ps | System population, maximum simultaneous # of occupants of space served by system | 80
D | Occupant diversity, ratio of system peak occupancy to sum of space peak occupancies, = Ps/SPz | 0.65574
Vou | Uncorrected outdoor air intake, = D*SRp*Pz +SRa*Az, cfm | 1402.6951
Vps | Total system primary flow to all zones, S Vpz, cfm | 2500 | Note: In VAV systems, Vps is equal to the fan airflow, and the formula in cell c40 needs to be replaced by this value.
Xs | Mixing ratio at primary air handler of uncorrected outdoor air intake to system primary flow, = Vou/Vps | 0.56108
SYSTEM EFFICIENCY
Evs | Zone ventilation efficiency, (Fa +Xs*Fb - Z*Fc)/Fa | 1.0065 | 1.0266 | 0.87091 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Ev | System ventilation efficiency, min(Evs) | 0.87091
Percent outdoor air intake
Vot | Minimum outdoor air intake, Vou/Ev, cfm | 1610.6172 |  | 64.42% | = Vot/Vps
| Space type | Rp (cfm/per) | Ra (cfm/ft2)
| Art classroom | 10 | 0.18
| Auditorium seating area | 5 | 0.06
| Bank vaults/safe deposit | 5 | 0.06
| Barber shop | 7.5 | 0.06
| Barracks sleeping areas | 5 | 0.06
| Bars, cocktail lounges | 7.5 | 0.18
| Beauty and nail salons | 20 | 0.12
| Bedroom/Living Room | 5 | 0.06
| Booking/waiting | 7.5 | 0.06
| Bowling alley (seating) | 10 | 0.12
| Cafeteria / fast food dining | 7.5 | 0.18
| Cell | 5 | 0.12
| Classrooms (age 9 plus) | 10 | 0.12
| Classrooms (ages 5-8) | 10 | 0.12
| Coin operated laundries | 7.5 | 0.06
| Computer (not printing) | 5 | 0.06
| Computer Lab. | 10 | 0.12
| Conference / meeting | 5 | 0.06
| Corridors | 0 | 0.06
| Courtrooms | 5 | 0.06
| Daycare (through age 4) | 10 | 0.18
| Dayroom | 5 | 0.06
| Disco/dance floors | 20 | 0.06
| Gambling casinos | 7.5 | 0.18
| Game arcades | 7.5 | 0.18
| Guard stations | 5 | 0.06
| Gym, stadium (play area) | 0 | 0.3
| Health club/aerobics room | 20 | 0.06
| Health club/weight rooms | 20 | 0.06
| Lecture Classroom | 7.5 | 0.06
| Lecture Hall (fixed seats) | 7.5 | 0.06
| Legislative chambers | 5 | 0.06
| Libraries | 5 | 0.12
| Lobbies | 5 | 0.06
| Lobbies/prefunction | 7.5 | 0.06
| Main entry lobbies | 5 | 0.06
| Mall common areas | 7.5 | 0.06
| Media Center | 10 | 0.12
| Multi-purpose assembly | 5 | 0.06
| Multi-use Assembly | 7.5 | 0.06
| Museums (Children’s) | 7.5 | 0.12
| Museums/Galleries | 7.5 | 0.06
| Music/theater/dance | 10 | 0.06
| Office space | 5 | 0.06
| Pet shops (animal areas) | 7.5 | 0.18
| Pharmacy (prep. area) | 5 | 0.18
| Photo studios | 5 | 0.12
| Places of religious worship | 5 | 0.06
| Reception areas | 5 | 0.06
| Restaurant dining rooms | 7.5 | 0.18
| Sales (except as below) | 7.5 | 0.12
| Science laboratories | 10 | 0.18
| Shipping/Receiving | 0 | 0.12
| Spectator areas | 7.5 | 0.06
| Sports arena (play area) | 0 | 0.3
| Stages, studios | 10 | 0.06
| Storage rooms | 0 | 0.12
| Supermarket | 7.5 | 0.06
| Swimming (pool & deck) | 0 | 0.48
| Telephone/data entry | 5 | 0.06
| Transportation waiting | 7.5 | 0.06
| Warehouses | 0 | 0.06
| Wood/metal shop | 10 | 0.18

## AppA SI
READ THIS FIRST To use this spreadsheet, identify the zones served by the system being designed and list them in row 4. Then select the space type using the pull down menus in row 5. For each zone, enter the values in all yellow shaded cells, plus the total number of occupants expected to be served by the system in cell C20. The values used for Vpz and Vpzm depend on whether one is designing a CAV or VAV system. Notes in bold text are included below that explain these distinctions. NOTE: Various sums and formulas in column C (in boxes) are based on the individual zone data entered from column C through column Z. If the system, has more than 24 zones, then the sums and formulas in column C need to be modified to include all the zones.
RESULTS
Vot | Minimum outdoor air intake, Vou/Ev, L/s | 280.2472
| Percent outdoor air intake, Vot/Vps | 11.68%
Ev | System ventilation efficiency | 0.83029
ZONE LEVEL
| Zones served by system | Zone 1 | Zone 2 | Zone 3 | Zone 4
| Space type (select from pull-down list) | Lobbies/prefunction | Office space | Classrooms (age 9 plus) | Conference / meeting | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space
Az | Floor area of zone, m2 | 100 | 100 | 100 | 50
Pz | Zone population, largest # of people expected to occupy zone | 20 | 4 | 20 | 10
Rp | People outdoor air rate from Table 6.1, L/s-person | 3.8 | 2.5 | 5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Ra | Area outdoor air rate from Table 6.1, L/s-m2 | 0.3 | 0.3 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Pz*Rp |  | 76 | 10 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Az*Ra |  | 30 | 30 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Voz | Outdoor airflow to the zone corrected for zone air distribution effectiveness, (Pz*Rp + Az*Ra)/Ez, L/s | 106 | 40 | 160 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vpz | Primary airflow to zone from air handler (intake plus recirculated air, but not local recirculation such as at mixing boxes), L/s. In VAV systems, use the design value. | 600 | 600 | 600 | 600
Vdz | Supply/discharge to zone including primary air Vpz and locally recirculated air, L/s. In VAV systems, use the design value. | 600 | 600 | 600 | 600
Vdzm | Minimum supply/discharge to zone used to calculate Ev, L/s. In CAV systems, Vdzm = Vdz. In VAV systems, Vdzm is the minimum expected value of Vdz. | 600 | 600 | 600 | 600
Zd | Outdoor air fraction required in air discharged to zone, = Voz/Vdzm | 0.17667 | 0.066667 | 0.26667 | 0.066667 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Ep | Primary air fraction to zone, = Vpz/Vdz (=1 for single duct and single zone systems) | 1 | 1 | 1 | 1 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Er | Fraction of secondary recirc to zone representative of system average, only applies if Ep<1. For plenum return =0. For duct return with local secondary recirc =1. | 0 | 0 | 0 | 0
Ez | Zone air distribution effectiveness, Table 6.2 | 1 | 1 | 1 | 1
Fa | Fraction of supply air to zone from sources outside zone, = Ep + (1-Ep)*Er | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fb | Fraction of supply air to zone from full mixed primary air, = Ep = Vpz/Vdz | 1 | 1 | 1 | 1 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Fc | Fraction of outdoor air to zone from sources outside zone, = 1 - (1-Ez) * (1-Er) * (1-Ep) | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SYSTEM LEVEL
Ps | System population, maximum simultaneous # of occupants of space served by system | 25
D | Occupant diversity, ratio of system peak occupancy to sum of space peak occupancies, = Ps/SPz | 0.46296
Vou | Uncorrected outdoor air intake, = D*SRp*Pz +SRa*Az, L/s | 232.6852
Vps | Total system primary flow to all zones, S Vpz, L/s | 2400 | Note: In VAV systems, Vps is equal to the fan airflow, and the formula in cell c40 needs to be replaced by this value.
Xs | Mixing ratio at primary air handler of uncorrected outdoor air intake to system primary flow, = Vou/Vps | 0.096952
SYSTEM EFFICIENCY
Evs | Zone ventilation efficiency, (Fa +Xs*Fb - Z*Fc)/Fa | 0.92029 | 1.0303 | 0.83029 | 1.0303 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Ev | System ventilation efficiency, min(Evs) | 0.83029
Percent outdoor air intake
Vot | Minimum outdoor air intake, Vou/Ev, L/s | 280.2472 |  | 11.68% | = Vot/Vps
| Space type | Rp (L/s-per) | Ra (L/s-m2)
| Art classroom | 5 | 0.9
| Auditorium seating area | 2.5 | 0.3
| Bank vaults/safe deposit | 2.5 | 0.3
| Barber shop | 7.5 | 0.3
| Barracks sleeping areas | 2.5 | 0.3
| Bars, cocktail lounges | 3.8 | 0.9
| Beauty and nail salons | 10 | 0.6
| Bedroom/Living Room | 2.5 | 0.3
| Booking/waiting | 3.8 | 0.3
| Bowling alley (seating) | 5 | 0.6
| Cafeteria / fast food dining | 3.8 | 0.9
| Cell | 2.5 | 0.6
| Classrooms (age 9 plus) | 5 | 0.6
| Classrooms (ages 5-8) | 5 | 0.6
| Coin operated laundries | 3.8 | 0.3
| Computer (not printing) | 2.5 | 0.3
| Computer Lab. | 5 | 0.6
| Conference / meeting | 2.5 | 0.3
| Corridors | 0 | 0.3
| Courtrooms | 2.5 | 0.3
| Daycare (through age 4) | 5 | 0.9
| Dayroom | 2.5 | 0.3
| Disco/dance floors | 10 | 0.3
| Gambling casinos | 3.8 | 0.9
| Game arcades | 3.8 | 0.9
| Guard stations | 2.5 | 0.3
| Gym, stadium (play area) | 0 | 0.3
| Health club/aerobics room | 10 | 0.3
| Health club/weight rooms | 10 | 0.3
| Lecture Classroom | 3.8 | 0.3
| Lecture Hall (fixed seats) | 3.8 | 0.3
| Legislative chambers | 2.5 | 0.3
| Libraries | 2.5 | 0.6
| Lobbies | 2.5 | 0.3
| Lobbies/prefunction | 3.8 | 0.3
| Main entry lobbies | 2.5 | 0.3
| Mall common areas | 3.8 | 0.3
| Media Center | 5 | 0.6
| Multi-purpose assembly | 2.5 | 0.3
| Multi-use Assembly | 3.8 | 0.3
| Museums (Children’s) | 3.8 | 0.6
| Museums/Galleries | 3.8 | 0.3
| Music/theater/dance | 5 | 0.3
| Office space | 2.5 | 0.3
| Pet shops (animal areas) | 3.8 | 0.9
| Pharmacy (prep. area) | 2.5 | 0.9
| Photo studios | 2.5 | 0.6
| Places of religious worship | 2.5 | 0.3
| Reception areas | 2.5 | 0.3
| Restaurant dining rooms | 3.8 | 0.9
| Sales (except as below) | 3.8 | 0.6
| Science laboratories | 5 | 0.9
| Shipping/Receiving | 0 | 0.6
| Spectator areas | 3.8 | 0.3
| Sports arena (play area) | 0 | 0.3
| Stages, studios | 5 | 0.3
| Storage rooms | 0 | 0.6
| Supermarket | 3.8 | 0.3
| Swimming (pool & deck) | 0 | 2.4
| Telephone/data entry | 2.5 | 0.3
| Transportation waiting | 3.8 | 0.3
| Warehouses | 0 | 0.3
| Wood/metal shop | 5 | 0.9